## Inputs
Sanitary / Industrial Wastewater Pump Station - Preliminary Design Inputs
Yellow cells are editable except the fixed external area assumption linked in B5. Placeholder values must be validated with survey, municipal criteria, and process-water data.
Wastewater Flow Inputs |  |  |  | Pump Sump / Control Inputs
Contributing industrial area (linked to fixed assumption) |  | m2 | Linked to fixed external assumption below; keep outside adjustable scenario inputs. | Sump internal diameter | 1.5 | m | Circular wet well diameter.
Unit wastewater allowance by area | 0.5 | L/m2/d | Replace with company water-use data or municipal design criterion if available. | Sump bottom elevation | 100 | m | Use project datum or temporary relative datum.
Number of employees | 0 | persons | Enter known staff count or test scenarios. | Pump stop elevation | 100.3 | m | Water level where pump stops.
Domestic flow per employee | 75 | L/p/d | Preliminary value for toilets/handwashing. Increase if showers/cafeteria are present. | Pump start elevation | 100.9 | m | Water level where lead pump starts.
Process wastewater | 0 | m3/d | Parts washing, floor washdown, process drains, etc. | High alarm elevation | 101.1 | m | Alarm level above pump start.
Peak factor | 4 | - | Preliminary peaking factor. Confirm with municipality/design criteria. | Inlet pipe invert at sump | 100.8 | m | Gravity inlet invert entering wet well.
Minimum practical pump flow | 2 | L/s | Small sewage pumps often have a practical minimum selected flow. | Pump discharge/force main invert | 100.75 | m | Approximate force-main outlet from station.
Design safety factor on flow | 1 | - | Optional design margin. | Pump efficiency | 0.6 | - | Overall preliminary efficiency.
Pretreatment / Settling Inputs |  |  |  | Force Main / Discharge Inputs
Pretreatment provided? | Yes/No | - | Use for settling tank, oil/grit separator, neutralization, or other industrial pretreatment. | Receiving MH water elevation | 103 | m | Use downstream hydraulic grade/tailwater if known.
Pretreatment inlet invert | 100.95 | m | Invert entering pretreatment unit. | Receiving MH invert | 102.7 | m | Invert in receiving manhole.
Pretreatment outlet invert | 100.85 | m | Invert leaving pretreatment unit. | Force main length | 30 | m | Total discharge pipe length.
Provided tank volume | 1.5 | m3 | Effective liquid volume. | Force main internal diameter | 0.075 | m | Use actual internal diameter.
Target detention at peak | 10 | min | Preliminary detention target. | Darcy friction factor f | 0.025 | - | Preliminary value; revise with pipe material/roughness.
Pretreatment headloss | 0.1 | m | Hydraulic loss through device/tank if applicable. | Minor loss coefficient K | 4 | - | Valves, bends, entrance, exit, check valve.
|  |  |  | Minimum target velocity | 0.6 | m/s | Common preliminary lower check for solids transport.
|  |  |  | Maximum target velocity | 2.5 | m/s | Common preliminary upper check for excessive losses.
Fixed External Assumptions (outside editable scenario inputs) |  |  |  | Design Criteria / Operational Targets
Fixed industrial/roof contributing area | 7600 | m2 | Owner-provided fixed value. Keep this constant unless the facility footprint is revised. | Maximum starts per hour (recommended) | 10 | starts/hr | Typical municipal preliminary target.
|  |  |  | Minimum stop submergence target | 0.3 | m | Protect pump hydraulics and avoid vortex/air entrainment.
|  |  |  | Minimum emergency storage time (alarm to inlet) | 10 | min | Preferred buffer before inlet surcharge at peak inflow.
|  |  |  | Motor service factor | 1.15 | - | Apply to preliminary motor sizing.
|  |  |  | Duty pumps in parallel (normal operation) | 1 | - | Use 1 for duty+standby; set >1 if pumps run in parallel.
|  |  |  | Standby pumps (N+1) | 1 | - | For redundancy check and procurement definition.
|  |  |  | Future flow factor | 1 | - | Multiply average flow to account for growth/uncertainty.
Note on B5: Used only as a preliminary industrial wastewater proxy, not roof runoff.
Note on F5: Circular wet well diameter.
Note on B6: Replace with company water-use data or municipal design criterion if available.
Note on F6: Use project datum or temporary relative datum.
Note on B7: Enter known staff count or test scenarios.
Note on F7: Water level where pump stops.
Note on B8: Preliminary value for toilets/handwashing. Increase if showers/cafeteria are present.
Note on F8: Water level where lead pump starts.
Note on B9: Parts washing, floor washdown, process drains, etc.
Note on F9: Alarm level above pump start.
Note on B10: Preliminary peaking factor. Confirm with municipality/design criteria.
Note on F10: Gravity inlet invert entering wet well.
Note on B11: Small sewage pumps often have a practical minimum selected flow.
Note on F11: Approximate force-main outlet from station.
Note on B12: Optional design margin.
Note on F12: Overall preliminary efficiency.
Note on B19: Use for settling tank, oil/grit separator, neutralization, or other industrial pretreatment.
Note on F19: Use downstream hydraulic grade/tailwater if known.
Note on B20: Invert entering pretreatment unit.
Note on F20: Invert in receiving manhole.
Note on B21: Invert leaving pretreatment unit.
Note on F21: Total discharge pipe length.
Note on B22: Effective liquid volume.
Note on F22: Use actual internal diameter.
Note on B23: Preliminary detention target.
Note on F23: Preliminary value; revise with pipe material/roughness.
Note on B24: Hydraulic loss through device/tank if applicable.
Note on F24: Valves, bends, entrance, exit, check valve.
Note on F25: Common preliminary lower check for solids transport.
Note on F26: Common preliminary upper check for excessive losses.

## Design Summary
Preliminary Pump Station Design Summary
Flow Results |  |  | Wet-Well / Pump Cycle Results
Area-based flow | m3/d | A preliminary proxy only. | Active depth | m | Start minus stop.
Employee domestic flow | m3/d |  | Active wet-well volume | m3
Total average flow | m3/d | Includes future-flow factor. | Storage above alarm to inlet | m3 | Simple emergency buffer before inlet surcharge.
Peak influent flow | L/s |  | Fill time pump off | min
Selected pump flow | L/s |  | Drawdown time pump on | min
Selected pump flow | m3/s |  | Approx starts per hour | starts/hr
Average daily volume | m3/d |  | Start level above inlet invert | m | Positive means start level above inlet invert.
|  |  | Stop submergence above bottom | m
|  |  | Emergency storage time (alarm to inlet) | min | Time from high alarm to inlet surcharge at peak inflow.
|  |  | Required active volume @ starts limit | m3 | Minimum active volume to keep starts/hr within target.
|  |  | Active volume margin vs starts limit | m3 | Positive means wet-well active storage is adequate.
Force Main / TDH Results |  |  | Pretreatment Results
Force main area | m2 |  | Pretreatment invert drop | m
Force main velocity | m/s |  | Average detention | min
Velocity head | m |  | Peak detention | min
Friction headloss | m | Darcy-Weisbach. | Required volume at target | m3
Minor losses | m |  | Volume margin | m3 | Positive is OK.
Static lift | m | Receiving water level minus pump stop elevation. | Pretreatment status | -
Total dynamic head | m
Approx hydraulic power | kW | Water power only. | Best-fit operating flow (from curve) | L/s | Closest intersection between trial pump and system curves.
Approx motor power | kW | Preliminary. | Best-fit system TDH | m
Force main internal volume | m3 | Useful for septicity and retention checks. | Best-fit motor power (with service factor) | kW | Preliminary motor sizing check.
Force-main retention at average flow | min | Long retention can drive odor and corrosion risk. | Head residual at best fit (pump-system) | m | Absolute value near zero indicates good match.
Force-main retention at selected flow | min | During pump operation.
Duty pump flow per operating pump | L/s | Use for vendor pump selection when multiple duty pumps run.
Design Flags
Velocity check
Pump cycling check
Wet well level check
Inlet surcharge warning
Pretreatment check
Submergence check
Emergency storage check
Operating point check

## Pump Curve
System Curve and Trial Pump Curve
Flow | Flow | Velocity | Static Head | Friction + Minor | System TDH | Trial Pump Head | Difference | Abs Difference | Operating Point (auto-fit) | Replace column G with manufacturer data when available.
L/s | m3/s | m/s | m | m | m | m | m | m | Based on minimum absolute head difference in column I.
0
0.5
1
1.5 | [8 empty] | Best-fit row
2 | [8 empty] | Operating flow (L/s)
2.5 | [8 empty] | System TDH at operating point (m)
3 | [8 empty] | Pump head at operating point (m)
3.5 | [8 empty] | Head residual (pump - system) (m)
4 | [8 empty] | Flow per duty pump (L/s)
4.5 | [8 empty] | Estimated motor power at op. (kW)
5
5.5
6
6.5
7
7.5
8
8.5
9
9.5
10

## Croquis
Concept Croquis - Sanitary / Industrial Wastewater Pumping System
Pump Sump / Wet Well lead pump + standby pump start/stop controls
| Industrial Building floor drains / sanitary fixtures process wastewater if connected |  |  | Pretreatment / Settling (optional or municipal requirement) | [5 empty] | Receiving Manhole |  |  | Municipal Sewer / Approved Discharge
|  |  | gravity |  |  | gravity |  |  | force main |  |  | gravity / pressure
| Flow inputs |  |  | Pretreatment volume | [5 empty] | Receiving water level
|  | m2 industrial area |  |  | m3 |  | Pump start |  |  |  | m
[8 empty] | m |  | Force main diameter
Industrial area used in sizing is fixed external assumption. |  | m2 |  |  |  |  | Pump stop |  |  |  | m
[8 empty] | m |  | Force main length
[7 empty] | Sump bottom |  |  |  | m
m